TEST REPORT

This Laboratory is accredited by the National Association of Testing Authorities, Australia. Accreditation No:  14953. The tests reported herein have been performed in accordance with its scope of accreditation. This document shall not be reproduced, except in full.

CLEAN ROOM UNDER TEST

CLASSIFICATION:					STANDARD:

DATE:		  		                (      )	LAMINAR FLOW CLEAN ROOM			AS1386

CLASS:				                 (     )       NON LAMINAR FLOW CLEAN ROOM		AS1386

LOCATION:

CLIENT:

ADDRESS:

CONTACT:

PHONE NO:

TEST REPORT NO:

Page  1  of  8

ROOM LOCATION:

TEST SUMMARY

CLASSIFICATION:							MINIMUM PASS:

(      )	LAMINAR FLOW CLEAN ROOM

(      )	NON LAMINAR FLOW CLEAN ROOM

TEST DESCRIPTION:							PASS		FAIL		N/A

A)	Air Velocity, Uniformity & Pressure				(        )		(        )		(        )

B)	Air Changes per Hour						(        )		(        )		(        )

C)	H.E.P.A. Filter Integrity – Supply Air				(        )		(        )		(        )

D)	H.E.P.A. Filter Integrity – Return / Exhaust Air			(        )		(        )		(   *  )

E)	Plan Layout / Air Pressure Differentials				(        )		(        ) 		(        )

F)	Total Air Quantities						(        )		(        )		(        )

G)	Airborne Particulate Count in Work Zone				(        )		(        )		(        )

H)	Class 3.5 or other Air Requirements				(        )		(        )		(        )

(see note 3 below)

J)	Light Intensity							(        )		(        )		(        )

K)	Sound Level							(        )		(        )		(        )

L)	Test Instruments						(        )		(        )		(        )

Note:	1)	( / ) 	Not applicable or not scheduled.

2)	( * )	Indicates relevant result or test method.

3)	Compliance to Class 3.5 (U.S. Fed Standard Class 100). Air cleanliness requirements is established on the basis of compliance to tests A, C and F, as detailed above.

TESTED BY:	      	                               N.A.T.A SIGNATORY:				DATE:

NAME (PRINT):

TEST REPORT NO:				             DUE DATE OF NEXT TEST:

Page  2  of  8

| AIR CHANGE RATE CALCULATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DATE: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROOM | FILTER | FILTER |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | AVE | FLOW | ROOM | AIR |
|  | No: | AREA |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | VEL | RATE | VOL | CHANGE |
|  |  | (M2) | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | (m/s) | (m3/s) | (m3) | RATE (ACR) |
| Cleanroom 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TOTAL |  |  |  |
| Cleanroom 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TOTAL |  |  |  |
| Airlock |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  | TOTAL |  |  |  |
| Pressures |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| ROOM | Pressure (Pa) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cleanrm 1 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Cleanrm 2 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Airlock |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

TEST REPORT NO:

TESTED BY:										DATE:

Page  3  of  8

HEPA FILTER INTEGRITY

AS1807.6 – DETERMINATION OF INTEGRITY OF TERMINALLY MOUNTED HEPA FILTER INSTALLATIONS

FILTER

FILTER

FILTER

FILTER

FILTER

FILTER

FILTER

FILTER

FILTER

FILTER

Filter Sizes:

TEST REPORT NO:

Page  4  of  8

LIGHTING INTENSITY

METHOD:			AS1807.15 – DETERMINATION OF ILLUMINANCE

- ALL LIGHTING INTENSITIES ARE SHOWN AS UNITS OF LUX

2.				CONDITION OF LIGHTING INSTALLATION	-

3.				MINIMUM LIGHTING INTENSITY =

MINIMUM REQUIREMENT OF STANDARD = 800 LUX

THEREFORE RESULTS OBTAINED = PASS

| POSITION NO: | READING (Lux) | POSITION NO: | READING (Lux) |
| --- | --- | --- | --- |
| P.1 |  | P.10 |  |
| P.2 |  | P.11 |  |
| P.3 |  | P.12 |  |
| P.4 |  | P.13 |  |
| P.5 |  | P.14 |  |
| P.6 |  | P.15 |  |
| P.7 |  | P.16 |  |
| P.8 |  | P.17 |  |
| P.9 |  | P.18 |  |

SOUND LEVELS IN CLEANROOM

METHOD:				AS1807.16:	DETERMINATION OF SOUND LEVEL IN CLEANROOMS

CALIBRATION CHECK PRIOR TO EACH INDIVIDUAL READING	-	YES (    )		NO (     )

READING =

MAXIMUM ALLOWABLE READING = 68.0 dB(A)		MAXIMUM READING OBTAINED =

THEREFORE RESULTS =

| POSITION NO: | READING dB(A) | POSITION NO: | READING dB(A) |
| --- | --- | --- | --- |
| P.1 |  | P.10 |  |
| P.2 |  | P.11 |  |
| P.3 |  | P.12 |  |
| P.4 |  | P.13 |  |
| P.5 |  | P.14 |  |
| P.6 |  | P.15 |  |
| P.7 |  | P.16 |  |
| P.8 |  | P.17 |  |
| P.9 |  | P.18 |  |

TEST REPORT NO:

Page  5  of  8

AIRBOURNE PARTICLE COUNTS IN WORK ZONE

The following tests were conducted using a calibrated particle analyser Serial No:

Each test was a 10 litre sample.

Tests Used:

Australian Standard AS1386 – 1989, Cleanrooms and clean workstations:

AS1386.1 – 1989:	Part 1: Principle of clean space control.

AS1386.2 – 1989:	Part 2: Laminar flow cleanrooms.

AS1386.3 – 1989:	Part 3: Non laminar flow cleanrooms – Class 350 and cleaner.

AS1386.4 – 1989:	Part 4: Non laminar flow cleanrooms – Class 3500.

AS1807.8 – 2000:	Particle counting in work zone by automatic particle counter.

| SAMPLE POSITION | PARTICLE COUNT (PARTICLES) 0.5µm 5.0µm |  | PARTICLE LITRE 1 LITRE/SAMPLE 0.5µm 5.0µm |  | SAMPLE POSITION | PARTICLE COUNT (PARTICLES) 0.5µm 5.0µm |  | PARTICLE LITRE 1 LITRE/SAMPLE 0.5µm 5.0µm |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| P.1 |  |  |  |  | P.10 |  |  |  |  |
| P.2 |  |  |  |  | P.11 |  |  |  |  |
| P.3 |  |  |  |  | P.12 |  |  |  |  |
| P.4 |  |  |  |  | P.13 |  |  |  |  |
| P.5 |  |  |  |  | P.14 |  |  |  |  |
| P.6 |  |  |  |  | P.15 |  |  |  |  |
| P.7 |  |  |  |  | P.16 |  |  |  |  |
| P.8 |  |  |  |  | P.17 |  |  |  |  |
| P.9 |  |  |  |  | P.18 |  |  |  |  |

Note:	All particle counts taken with the cleanroom in ‘Operation’ mode.

TESTED BY:

TEST REPORT NO:

Page  6  of  8

CLEANROOM COMPLEX

PLAN VIEW – NOT TO SCALE

TEST REPORT NO:

Page  7  of  8

TEST EQUIPMENT

SERIAL NO:	CALIBRATION REPORT NO:	DATE OF NEXT CAL.

1.           AIRBOURNE PARTICLE ANALYSER:

2.          AEROSOL PHOTOMETER:

3.	D.O.P. AEROSOL GENERATOR:			                                 IN HOUSE

- ANEMOMETER:

5.	DIGITAL MANOMETER 0 to 1KPa:

6.	ILLUMINANCE METER:

7.	SOUND LEVEL METER:

8.	SOUND CALIBRATOR:

CONCLUSION:

| TEST | STANDARD | DESCRIPTION: | PAGE NO: | PASS / FAIL |
| --- | --- | --- | --- | --- |
| A | AS1807.3 | AIR VELOCITY | 3 |  |
| * B | GMP AS1807 | AIR CHANGE RATE | 3 |  |
| C | AS1807.6 | HEPA FILTER INTEGRITY | 4 |  |
| F | AS1807.10 | ROOM AIR DIFFERENTIALS | 3 & 7 |  |
| G | AS1807.8 | PARTICLE COUNTS IN WORK ZONE | 5 |  |
| J | AS1807.15 | LIGHT INTENSITY | 6 |  |
| K | AS1807.16 | SOUND LEVEL | 6 |  |

The above tests show that the room complies to Class 3500    AS1386.6 – 1989.

NOTE:	Test B – Marked thus * not covered by N.A.T.A. scope of accreditation.

TEST REPORT NO:

Page  8  of  8