TEST REPORT

Page  1  of  3

REPORT NO:					TEST DATE:				SERIAL NO:

EQUIPMENT CLASSIFICATION:	Fume Cupboard

TEST REQUIREMENTS:	AS2243.8							MODEL NO:

MANUFACTURER:									LOCATION:

CLIENT:											PHONE NO:

ADDRESS:										CONTACT:

| TEST METHOD | TEST DESCRIPTION | REQUIREMENT | READING | RESULT |
| --- | --- | --- | --- | --- |
| AS2243.8 App E | Average Air Velocity And Uniformity | Average ≥ 0.50 m/sec Uniformity Max: % Min: % | m/sec + % - % |  |
| AS2243.8 App F | Smoke Test | As per Appendix F | N/A |  |
| AS1807.15 | Lighting Intensity: | Minimum 400 lux | Lux |  |
| AS1807.20 | Sound Level: | Maximum 62 dB(A) | dB(A) |  |

This Laboratory is accredited by the National Association of Testing Authorities, Australia. Accreditation No:  14953. The tests reported herein have been performed in accordance with its scope of accreditation. This document shall not be reproduced, except in full.

TESTED BY:				N.A.T.A. SIGNATORY:					DATE:

NAME (PRINT):